## Consumption
				Running power	92.65	W
				Standby power	3.13	W

Component	Model (Make)	Rating description	Qnty	Volts	Amps	Power, W	Total, W
Datalogger	CR3000	10-16Vdc; current depends	1	12	0.010	0.12	0.12	Core devices
Datalogger ethernet module	NL115	depends; worst case: 43 mA @ 12Vdc	1	12	0.043	0.52	0.52
GPS receiver	GPS16x-HVS	8-40Vdc @ 65mA	1	12	0.065	0.78	0.78
Pressure sensor	PX409-030A5V	10-30Vdc @ 10mA	2	12	0.010	0.12	0.24
Solar regulator	SunSaver	per CSI tech note: 6-10 mA continuously	1	12	0.010	0.12	0.12
Sonic anemometer	81000VRE	12-24Vdc @ 110mA max	1	12	0.110	1.32	1.32
Temp/RH sensor	HMP155A	7-28Vdc @ <=3mA	1	12	0.003	0.04	0.04

Fast-acting valve	(Parker)	12Vdc @ 1000mA	2	12	1.000	12	24	Off in stand-by
Fast-acting valve	(Asco)	10.6 Watts	0	10.6	1.000	10.6	0
Mass flow controller	MC-20SLPM-D	12-30Vdc @ 250mA	1	12	0.250	3	3
Pump	KNF	12Vdc @ 5.2A	1	12	5.200	62.4	62.4
Valve control relay	ODC5	12mA @ nominal logic voltage (1mA off-state leakage)	2	5	0.012	0.06	0.12

## PV system
Max consumption	92.65	W		Temp. derating multiplier [1]				Reference
	7.72	Amps		Degrees	Degrees				sun hours/day
Standby consumption	3.13	W		F	C	Multiplier		Location	annual mean	winter
	0.26	Amps		80	26	1		Pullman, WA	4	2	[5, 6], [4]
				70	21.2	1.04
Operating conditions				60	15.6	1.11
Running hours of pump per day	24	hr/day		50	10	1.19
Watt hours needed per day	2224	W*hr/day		40	4.4	1.3
				30	-1.1	1.4
				20	-6.7	1.59

Battery bank requirement [1,2]				Selected battery characteristics
Battery bank voltage	12	V		Type	Surrette S-550
Days without sun	3	days		Voltage	6	Volts
Depth of discharge	50%			Amp-hour	524	Ahr
Temperature multiplier	1.59			Number of	4	batteries
Battery bank size	1768	A*hr		Total reserve	1048	Ahr
				Req'd #	7	batteries

Solar array sizing (annual mean) [2]				Selected PV panel characteristics
Sun hours per day	4	hr/day		Type	Astronergy
Generation requirement	556	W/hr		Current	8.53	Amps
Required # of solar panels	2	panels		Voltage	35.77	Volts
Max amperage to PV controller	17	Amps		Power	305	Watts

Solar array sizing (winter worst-case) [2]				Charge controller min. amperage
Sun hours per day	2	hr/day		43	Amps in	80%
Generation requirement	1112	W/hr		0	Amps out	capacity
Required # of solar panels	4	panels
Max amperage to PV controller	34	Amps

Wire size requirements [3]
Max voltage across wire	35.77	Volts

[1] http://rimstar.org/renewnrg/sizing_select_batteries_for_off_grid_solar_system.htm
[2] http://pdf.wholesalesolar.com/Download%20folder/System_Worksheet.pdf
[3] http://rimstar.org/renewnrg/solar_voltage_drop_table_calculator_wire_sizing_for_dc.htm
[4] http://pvwatts.nrel.gov/pvwatts.php
[5] http://www.ecy.wa.gov/climatechange/maps/solar/solar_state.pdf
[6] http://www.nrel.gov/gis/images/map_pv_national_hi-res_200.jpg