## Consumption
[7 empty] | Running power | 73.356 | W
[7 empty] | Standby power | 3.132 | W
Component | Model (Make) | Rating description | Qnty | Volts | Amps | Power, W | Run time | Total, W
Datalogger | CR3000 | 10-16Vdc; current depends | 1 | 12 | 0.01 | 0.12 | 100% | 0.12 | Core devices
Datalogger ethernet module | NL115 | depends; worst case: 43 mA @ 12Vdc | 1 | 12 | 0.043 | 0.516 | 100% | 0.516
GPS receiver | GPS16x-HVS | 8-40Vdc @ 65mA | 1 | 12 | 0.065 | 0.78 | 100% | 0.78
Pressure sensor | PX409-030A5V | 10-30Vdc @ 10mA | 2 | 12 | 0.01 | 0.12 | 100% | 0.24
Solar regulator | SunSaver | per CSI tech note: 6-10 mA continuously | 1 | 12 | 0.01 | 0.12 | 100% | 0.12
Sonic anemometer | 81000VRE | 12-24Vdc @ 110mA max | 1 | 12 | 0.11 | 1.32 | 100% | 1.32
Temp/RH sensor | HMP155A | 7-28Vdc @ <=3mA | 1 | 12 | 0.003 | 0.036 | 100% | 0.036
Fast-acting valve | (Parker) | 12Vdc @ 1000mA | 2 | 12 | 1 | 12 | 20% | 4.8 | Off in stand-by
Fast-acting valve | (Asco) | 10.6 Watts | 0 | 10.6 | 1 | 10.6 | 20% | 0
Valve control relay | ODC5 | 12mA @ nominal logic voltage (1mA off-state leakage) | 2 | 5 | 0.012 | 0.06 | 20% | 0.024
Mass flow controller | MC-20SLPM-D | 12-30Vdc @ 250mA | 1 | 12 | 0.25 | 3 | 100% | 3
Pump | KNF | 12Vdc @ 5.2A | 1 | 12 | 5.2 | 62.4 | 100% | 62.4
Note on H13: Patrick O'Keeffe: Assuming vertical wind speed is normally distributed and deadband multiplier is 0.85

## PV system
Max consumption | 73.356 | W | Temp. derating multiplier [1] |  |  | Reference
| 6.113 | Amps | Degrees | Degrees |  |  | sun hours/day
Standby consumption | 3.132 | W | F | C | Multiplier | Location | annual mean | winter
| 0.261 | Amps | 80 | 26 | 1 | Pullman, WA | 4 | 2 | [5, 6], [4]
|  |  | 70 | 21.2 | 1.04
Operating conditions |  |  | 60 | 15.6 | 1.11
Running hours of pump per day | 24 | hr/day | 50 | 10 | 1.19
Watt hours needed per day | 1760.544 | W*hr/day | 40 | 4.4 | 1.3
|  |  | 30 | -1.1 | 1.4
|  |  | 20 | -6.7 | 1.59
Battery bank requirement [1,2] |  |  | Selected battery characteristics
Battery bank voltage | 12 | V | Type | Surrette S-550
Days without sun | 3 | days | Voltage | 6 | Volts
Depth of discharge | 50% |  | Amp-hour | 524 | Ahr
Temperature multiplier | 1.59 |  | Number of | 4 | batteries
Battery bank size | 1399.6325 | A*hr | Total reserve | 1048 | Ahr
|  |  | Req'd # | 5.3421 | batteries
Solar array sizing (annual mean) [2] |  |  | Selected PV panel characteristics
Sun hours per day | 4 | hr/day | Type | Astronergy
Generation requirement | 440.136 | W/hr | Current | 8.53 | Amps
Required # of solar panels | 2 | panels | Voltage | 35.77 | Volts
Max amperage to PV controller | 17.06 | Amps | Power | 305 | Watts
Solar array sizing (winter worst-case) [2] |  |  | Charge controller min. amperage
Sun hours per day | 2 | hr/day | 31.9875 | Amps in | 80%
Generation requirement | 880.272 | W/hr | 0 | Amps out | capacity
Required # of solar panels | 3 | panels
Max amperage to PV controller | 25.59 | Amps
Wire size requirements [3]
Max voltage across wire | 35.77 | Volts
[1] http://rimstar.org/renewnrg/sizing_select_batteries_for_off_grid_solar_system.htm
[2] http://pdf.wholesalesolar.com/Download%20folder/System_Worksheet.pdf
[3] http://rimstar.org/renewnrg/solar_voltage_drop_table_calculator_wire_sizing_for_dc.htm
[4] http://pvwatts.nrel.gov/pvwatts.php
[5] http://www.ecy.wa.gov/climatechange/maps/solar/solar_state.pdf
[6] http://www.nrel.gov/gis/images/map_pv_national_hi-res_200.jpg