Photovoltaic system for low power consumption configuration
300W solar panel
ground fault
protection device (GFPD)
surge suppressor
battery monitor
10A solar controller
10A
breaker
2A fast-blow inline fuse
10A
breaker
3A
breaker
GFCI
outlet
125A
inverter
breaker
6V batteries, in series
Long extension cord to tower
100A/100mV
shunt
AC
switch
300W inverter
Notes:
Per MorningStar "Parallel Battery String Wiring for Optimal Charging" technical note, charge controller and loads are connected 'diagonally' across parallel string battery bank.
Wiring diagram of MidNite Solar MNDC power center was heavily referenced
Inverter breaker is part of the MNDC power center, smallest size available
Inverter manual specifies 100A fuse; need to determine 125A breaker is acceptable
Breaker to GFCI outlet is in place of 3A fuse specified by inverter manual
GFPD added to satisfy NEC2008, requires proper site grounding
Solar Batt. Load
+ – + – + –
DC
AC
on/off
B2+
B1+
SIG
G2
G1
+
–
+
–
+
–
+
–
63A 0.5A